## Sheet1
See https://github.com/DoESLiverpool/somebody-should/issues/1529 for details
|  |  |  | Portable/Fixed/Stationary/IT |  | RPE | Rins | Ileak
Location | Item ID | Item description | Class | Type of Equipment | Visual | Earth ohm | Insulation Mohm | Leak mA | Polarity | Pass/Fail | Test Date | Tester | Issue # | Notes
Main Room | 1 | Morphy Richards Turbosteam iron | I | Portable | Pass | 0.01 | >20 | 0.06 | N/A | Pass | 2021-09-23 | PRG
Main Room | 2 | Wilko Travel Steam Iron | I | Portable | Pass | 0.01 | >20 | 0.05 | N/A | Pass | 2021-09-23 | PRG
| 3 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-09-23 | PRG
| 4 | PixMax Heatpress Controller | I | Stationary | Pass | >20 |  |  |  | Fail | 2022-05-21 | AMc | 1701 | Earth seems not to be connected
Main Room | 5 | Pen Plotter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-09-07 | AMc
| 6 | Fig 8 lead | II | Portable | Pass | N/A | >20 | N/A | N/A | Pass | 2023-09-07 | AMc
| 7 | does-laptop-5 | II | Portable | Pass | N/A | >20 | 0.05 | N/A | Pass | 2021-09-23 | PRG
| 8 | Cloverleaf lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-09-23 | PRG
| 9 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-09-09 | AMc
Recess | 10 | HP5IN1 Heatpress | I | Stationary | Pass | 0.01 | >20 | 0.07 | N/A | Pass | 2021-09-23 | AMc
| 11 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-09-09 | AMc
Recess | 12 | St. Margaret Heatpress | I | Stationary | Pass | 0.06 | >20 | 0.17 | N/A | Pass | 2023-09-09 | AMc
| 13 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-09-09 | AMc
Recess | 14 | Hettie Mug Heatpress | I | Stationary | Pass | 0.01 | >20 | 0.03 | N/A | Pass | 2023-09-09 | AMc
| 15 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-10-07 | AMc
Recess | 16 | aMW 17" Monitor | I | Stationary | Pass | 0.01 | >20 | 0.22 | N/A | Pass | 2021-10-07 | AMc
| 17 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-10-07 | AMc
Recess | 18 | Roland Vinyl Cutter | I | Stationary | Pass | 0.01 | >20 | 0.74 | N/A | Pass | 2021-10-07 | AMc
| 19 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-10-07 | AMc
Recess | 20 | Vinyl-cutter PC | I | Stationary | Pass | 0.01 | >20 | 0.67 | N/A | Pass | 2021-10-07 | AMc
Recess | 21 | Vinyl-cutter 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-10-07 | AMc
Recess | 22 | Phone-case heatpress | I | Portable | Pass | >20 | >20 | 0.03 | N/A | Fail | 2021-10-07 | AMc | 1617 | Was hard to find a metal test point on the case
Recess | 23 | Minishot injection moulder | I | Stationary | Fail | [5 empty] | 2021-10-07 | AMc |  | Partially disassembled, so didn't test further
Recess | 24 | Acrylic strip heater | I | Portable | Pass | 0.01 | >20 | 0.04 | N/A | Pass | 2021-10-07 | AMc
| 25 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-09-09 | AMc
Recess | 26 | Acer X203H monitor | I | Stationary | Pass | 0.05 | >20 | 0.19 | N/A | Pass | 2023-09-09 | AMc
Recess | 27 | 4-way "Extension 2" | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-09-09 | AMc
Recess | 28 | Brother label printer | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-09-09 | AMc
Recess | 29 | Dymo label printer | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-09-09 | AMc
Recess | 30 | Harry Plotter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-09-09 | AMc
| 31 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-09-09 | AMc
Recess | 32 | Bella sublimation printer | I | Stationary | Pass | 0.07 | >20 | 0.2 | N/A | Pass | 2023-09-09 | AMc
Recess | 33 | Heatpress 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-09-09 | AMc
| 34 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-09-09 | AMc
Recess | 35 | Sublimation printer PC | I | Stationary | Pass | 0.01 | >20 | 0.68 | N/A | Pass | 2023-09-09 | AMc
Recess | 36 | Recess 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-10-07 | AMc
Recess | 37 | Bookcase-of-Things 6-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-10-07 | AMc
CNC room | 38 | Drill Sergeant | I | Stationary | Pass | 0.01 | >20 | 0.04 | N/A | Pass | 2021-11-04 | AMc
CNC room | 39 | Hilka 6" bench grinder | I | Stationary | Pass | 0.01 | >20 | 0.06 | N/A | Pass | 2021-11-04 | AMc
CNC room | 40 | Drill press 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-04 | AMc
| 41 | Energer Jigsaw | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
| 42 | Black & Decker finishing sander | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
CNC room | 43 | Clarke sander | I | Stationary | Pass | 0.01 | >20 | 0.09 | N/A | Pass | 2021-11-04 | AMc
| 44 | 650W Powertool drill | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
| 45 | Cocraft HMD150 | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
| 46 | Macallister MSCS1200 circular saw | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
| 47 | Black & Decker KW800 router | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
| 48 | Black & Decker Scorpion | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
| 49 | Black & Decker olive jigsaw | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
| 50 | Black & Decker KS400E jigsaw | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
| 51 | Tacklife palm sander | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-04 | AMc
Main room | 52 | Desktop extension on desk next to coffee machine | Ext | Stationary | Pass | 0.01 | >20 | N/A | Open | Pass | 2022-05-21 | AMc | 1626
CNC room | 53 | Laser-room window 4-way | Ext | Stationary | Pass | 0.01 | 0.43 | N/A | Good | Pass | 2021-11-11 | RC
| 54 | Porter Cable vacuum cleaner | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-11 | RC
| 55 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-11 | AMc
CNC room | 56 | Hanns G monitor | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-11 | AMc
CNC room | 57 | Rexon scrollsaw | I | Stationary | Pass | 0.69 | >20 | 0.04 | N/A | Pass | 2021-11-11 | RC
| 58 | Einhell heatgun | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-11 | RC
| 59 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 60 | T-962 Reflow Oven | I | Portable | Pass | 0.01 | >20 | 0.05 | N/A | Pass | 2021-11-13 | AMc
| 61 | Challenge fan heater | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 62 | FeelTech FY3200S signal generator | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 63 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 64 | Tektronix 2232 oscilloscope | I | Portable | Pass | 0.01 | >20 | 0.75 | N/A | Pass | 2021-11-13 | AMc
| 65 | Farnell bench power supply | I | Portable | Pass | 0.05 | >20 | 0.12 | N/A | Pass | 2021-11-13 | AMc
| 66 | Workshop bench 4-way | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 67 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 68 | Amrel LPS301 bench power supply | I | Portable | Pass | 0.01 | >20 | 0.75 | N/A | Pass | 2021-11-13 | AMc
| 69 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 70 | Philips PM3302 oscilloscope | I | Portable | Pass | 0.01 | >20 | 0.05 | N/A | Pass | 2021-11-13 | AMc
| 71 | Rectangular illuminated loupe | I | Portable | Pass | 0.05 | >20 | 0.04 | N/A | Pass | 2021-11-13 | AMc
| 72 | Montgolfier hot air gun | I | Portable | Pass | 0.01 | >20 | 0.04 | N/A | Pass | 2021-11-13 | AMc
| 73 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 74 | Thermaltronics soldering iron | I | Portable | Pass | 0.01 | >20 | 0.45 | N/A | Pass | 2021-12-02 | AMc | 1627
| 75 | Soldering station fans | I | Stationary | Pass | 0.01 | >20 | 0.05 | N/A | Pass | 2021-11-13 | AMc
| 76 | Sony AC-VQ850 charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 77 | W.E.R. SMD rework station | I | Portable | Pass | 0.01 | >20 | 0.05 | N/A | Pass | 2021-11-13 | AMc
| 78 | RS Soldering Station | I | Portable | Pass | 0.01 | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 79 | Bronze illuminated loupe | I | Portable | Pass | 0.01 | >20 | 0.06 | N/A | Pass | 2021-11-13 | AMc
| 80 | Tripod-mounted lamp | I | Portable | Fail |  |  |  |  | Fail | 2021-11-13 | AMc | 1628
| 81 | Soldering station 10-way extension | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 82 | Bosch glue gun | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 83 | Elna Carina sewing machine | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 84 | Bernie sewing machine | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 85 | Ben New Home sewing machine | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 86 | Impy sewing machine | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 87 | Gertie industrial sewing machine | I | Stationary | Pass | 0.04 | >20 | 0.15 | N/A | Pass | 2021-11-13 | AMc
| 88 | Green anglepoise lamp | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-11-13 | AMc
| 89 | Workshop bench 2-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 90 | 2-way long extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-11-13 | AMc
| 91 | 20m 4-way extension reel | Ext | Portable | Pass | 0.21 | >20 | N/A | Good | Pass | 2023-09-07 | AMc
Dinky | 92 | Singer Tradition sewing machine | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-02 | AMc
Dinky | 93 | 8-way extension | Ext | Stationary | Pass | 0.01 | 2.85M | N/A | Good | Pass | 2021-12-02 | AMc
Dinky | 94 | Threaderick CNC embroidery machine | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-02 | AMc
Dinky | 95 | Small black fridge | I | Stationary | Pass | 0.01 | >20 | 0.06 | N/A | Pass | 2021-12-02 | AMc
Dinky | 96 | Kath Passap knitting machine | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-02 | AMc
| 97 | Mickey-mouse lead | IEC | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-02 | AMc
| 98 | Notevision projector | I | Portable | Pass | 0.01 | >20 | 0.35 | N/A | Pass | 2021-12-02 | AMc
| 99 | does-laptop-4 | II | Portable | Pass | N/A | >20 | 0.05 | N/A | Pass | 2021-12-02 | AMc
| 100 | Round illuminated loupe | I | Stationary | Pass | 0.01 | >20 | 0.04 | N/A | Pass | 2021-12-02 | AMc
| 101 | Mickey-mouse lead | IEC | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-02 | AMc
| 102 | Lenovo power supply | II | Portable | Pass | N/A | >20 | 0.06 | N/A | Pass | 2021-12-02 | AMc
| 103 | USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-02 | AMc
| 104 | Mickey-mouse lead | IEC | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-09 | AMc
| 105 | does-laptop-5 | II | Portable | Pass | N/A | >20 | 0.05 | N/A | Pass | 2021-12-09 | AMc
| 106 | Mickey-mouse lead | IEC | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-09 | AMc
| 107 | does-laptop-6 | II | Portable | Pass | N/A | >20 | 0.05 | N/A | Pass | 2021-12-09 | AMc
Dinky | 108 | Ariadne knitting machine | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
Dinky | 109 | Triangle USB charger behind TV | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
Under the Liverbird | 110 | Philips TV | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
Main room | 111 | Coffee machine | I | Stationary | Pass | 0.03 | >20 | 0.08 | N/A | Pass | 2021-12-09 | AMc |  | Re-tested after Paul Harvey's initial test
| 112 | Mickey-mouse lead | IEC | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-09 | AMc
| 113 | does-laptop-1 | II | Portable | Pass | N/A | >20 | 0.05 | N/A | Pass | 2021-12-09 | AMc
| 114 | Sean's old laptop | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
Main room | 115 | Stella drinks fridge | I | Stationary | Pass | 0.01 | >20 | 0.07 | N/A | Pass | 2021-12-09 | AMc
| 116 | RS rotary tool | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
| 117 | Philips cordless phone | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
| 118 | UMC TV | I | Portable | Pass | 0.01 | >20 | 0.23 | N/A | Pass | 2021-12-09 | AMc
| 119 | White HTC USB adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
| 120 | Edimax 5-port Ethernet Switch | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
| 121 | USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-09 | AMc
| 122 | Coffee machine sonoff | Sonoff | Stationary | Pass | 0.02 | >20 | 0.04 | N/A | Pass | 2021-12-09 | PRG
Dinky | 123 | Toshiba TV | II | Stationary | Pass | N/A | 8.25 | 0.23 | N/A | Pass | 2021-12-09 | PRG
Events Room | 124 | Crown blue 4-way 10m extension | Ext | Stationary | Pass | 0.07 | >20 | N/A | Good | Pass | 2023-09-09 | AMc | 1637
Events Room | 125 | Swan urn | I | Portable | Pass | 0.01 | >20 | 0.05 | N/A | Pass | 2021-12-23 | AMc
Events Room | 126 | Prodis drinks fridge | I | Stationary | Pass | 0.01 | >20 | 0.14 | N/A | Pass | 2021-12-23 | AMc
| 127 | Surge protect 4-way | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
| 128 | 4-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
| 129 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
| 130 | Hitachi projector | I | Portable | Pass | 0.01 | >20 | 0.88 | N/A | Pass | 2022-05-21 | AMc | 1638
| 131 | ABIS LED projector | I | Portable | Pass | 0.01 | >20 | 0.1 | N/A | Pass | 2021-12-23 | AMc
Events Room | 132 | LG L1717S monitor | I | Stationary | Pass | 0.01 | >20 | 0.39 | N/A | Pass | 2021-12-23 | AMc
| 133 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
| 134 | 4-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
| 135 | 6-way extension | Ext | Portable | Pass | 0.02 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
Events Room | 136 | Sheila's PC | I | Stationary | Pass | 0.01 | >20 | 0.4 | N/A | Pass | 2021-12-30 | AMc | 1639
Events Room | 137 | Switched 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
Events Room | 138 | Sophia's air compressor | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-30 | AMc | 1640
Events Room | 139 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
Events Room | 140 | Sheila's CW-3000 chiller | I | Stationary | Pass | 0.01 | >20 | 0.04 | N/A | Pass | 2021-12-23 | AMc
Events Room | 141 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
Events Room | 142 | Laser-cutter Sheila | I | Stationary | Pass | 0.01 | 1.01 | 1.23 | N/A | Pass | 2022-02-07 | AMc
| 143 | Blue Argos 1800W vacuum cleaner | II | Portable | Pass | N/A | >20 | 0 | N/A | Pass | 2021-12-23 | AMc
| 144 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
Events Room | 145 | Mackie PA speaker | I | Stationary | Pass | 0.01 | >20 | 0.16 | N/A | Pass | 2021-12-23 | AMc |  | There's some paint scratched off the heatsink on the back where you can get a decent earth connection for testing
| 146 | Surge protect 4-way | Ext | Portable | Pass | 0.01 | 1.28 | N/A | Good | Pass | 2021-12-23 | AMc
| 147 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
Events Room | 148 | Sony TV | I | Stationary | Pass | 0.01 | >20 | 0.51 | N/A | Pass | 2021-12-23 | AMc
| 149 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-23 | AMc
Events Room | 150 | Mackie PA speaker | I | Stationary | Pass | 0.01 | >20 | 0.16 | N/A | Pass | 2021-12-23 | AMc
Events Room | 151 | Denon amplifier | II | Stationary | Pass | N/A | >20 | 0.01 | N/A | Pass | 2021-12-23 | AMc
Events Room | 152 | img Stage Line mixer | II | Stationary | Pass | N/A | >20 | 0.01 | N/A | Pass | 2021-12-23 | AMc
| 153 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-30 | AMc
Events Room | 154 | PoE injector | II | Stationary | Pass | N/A | >20 | 0.04 | N/A | Pass | 2021-12-30 | AMc
Events Room | 155 | Sophia's extraction fan | I | Stationary | Pass | 0.01 | >20 | 0.06 | N/A | Pass | 2021-12-30 | AMc
| 156 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-30 | AMc
Events Room | 157 | Laser-cutter Sophia | I | Stationary | Pass | 0.01 | 1.21 | 2.36 | N/A | Fail | 2021-12-30 | AMc | 1643
| 158 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2021-12-30 | AMc
Events Room | 159 | Sophia's CW-3000 chiller | I | Stationary | Pass | 0.01 | >20 | 0.06 | N/A | Pass | 2021-12-30 | AMc
Events Room | 160 | Sheila's extraction fan | I | Stationary | Pass | 0.01 | >20 | 0.07 | N/A | Pass | 2021-12-30 | AMc
Events Room | 161 | Sheila's air compressor | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2021-12-30 | AMc
Main Room | 162 | Short 4-way extension under Liverbird | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-01-06 | AMc
| 163 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-01-06 | AMc
Main Room | 164 | Server under the Liverbird | II | Stationary | Pass | N/A | >20 | 0.11 | N/A | Pass | 2022-01-06 | AMc
Main Room | 165 | Nintendo Wii | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Main Room | 166 | Nintendo Wii | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Main Room | 167 | USB charger | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Main Room | 168 | Switched 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-01-06 | AMc
| 169 | IEC lead | IEC | Lead | Pass | 0.05 | >20 | N/A | Good | Pass | 2022-01-06 | AMc
| 170 | IEC extension | IEC | Lead | Pass | 0.06 | >20 | N/A | Good | Pass | 2022-01-06 | AMc
Main Room | 171 | Liverbird | I | Stationary | Pass | 0.05 | >20 | 0.68 | N/A | Pass | 2022-01-06 | AMc
Main Room | 172 | Ackers Bell | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Main Room | 173 | 12V adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
| 174 | Raspberry Pi adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Main Room | 175 | Network switch under Liverbird | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
| 176 | USB hub | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Main Room | 177 | Super Solid 8-way extension | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-01-06 | AMc
Main Room | 178 | Sonoff under the Liverbird | Sonoff | Stationary | Pass | 0.01 | >20 | 0.04 | N/A | Pass | 2022-01-06 | AMc
| 179 | HobbyKing 540W DC power supply | I | Portable | Pass | 0.09 | >20 | 0.61 | N/A | Pass | 2022-01-06 | AMc
Bookcase of Things | 180 | Makerbot CupCake 3D printer | I | Stationary | Pass | 0.01 | >20 | 0.6 | N/A | Pass | 2022-01-06 | AMc
Bookcase of Things | 181 | Smart display | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Bookcase of Things | 182 | DoES Tower | II | Stationary | Pass | N/A | >20 | 0.04 | N/A | Pass | 2022-01-06 | AMc
Bookcase of Things | 183 | LiteOn 12V adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Bookcase of Things | 184 | Museum in a Box | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Bookcase of Things | 185 | Testament to Manufacturing Variance | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
Bookcase of Things | 186 | USB adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-01-06 | AMc
| 187 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-02-07 | AMc
| 188 | PC power supply | I | Stationary | Pass | 0.01 | >20 | 2.04 | N/A | Pass | 2022-02-07 | AMc
| 189 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-02-07 | AMc
| 190 | Henry hoover | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
| 191 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
Room29 | 192 | OKI ES5462W printer | I | Stationary | Pass | 0.01 | >20 | 0.53 | N/A | Pass | 2022-03-10 | AMc
Room29 | 193 | HP OfficeJet 7510 printer | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
Room29 | 194 | Robot vacuum | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
| 195 | Linksys 5V 2.5A power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
| 196 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
| 197 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
| 198 | Lenovo power supply | II | Portable | Pass | N/A | >20 | 0.05 | N/A | Pass | 2022-03-10 | AMc
| 199 | 12V power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
| 200 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
| 201 | USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
Room29 | 202 | 4-way by printers | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
Room29 | 203 | Sit-stand desk | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
Room29 | 204 | AOC monitor | I | Stationary | Pass | 0.01 | >20 | 0.35 | N/A | Pass | 2022-03-10 | AMc
Room29 | 205 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
Room29 | 206 | LG IPS2343 monitor | II | Stationary | Pass | N/A | >20 | 0.18 | N/A | Pass | 2022-03-10 | AMc
Room29 | 207 | Oil-filled radiator (finned) | I | Portable | Pass | 0.01 | >20 | 0.07 | N/A | Pass | 2022-03-10 | AMc
| 208 | 4-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
| 209 | USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
| 210 | Samsung USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
Room29 | 211 | 4-way on Alex's desk | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
Room29 | 212 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
Room29 | 213 | Dell monitor | I | Stationary | Pass | 0.01 | >20 | 0.14 | N/A | Pass | 2022-03-10 | AMc
Room29 | 214 | ASUS 19.5V adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
Room29 | 215 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
Room29 | 216 | HP Pro PC (Alex's) | I | Stationary | Pass | 0.01 | >20 | 0.22 | N/A | Pass | 2022-03-10 | AMc
Room29 | 217 | Entuitive touchscreen monitor | I | Stationary | Pass | 0.01 | >20 | 0.17 | N/A | Pass | 2022-03-10 | AMc
Room29 | 218 | 4m 4-way on Alex's desk | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
Room29 | 219 | Linksys 5V 2.5A power adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
Room29 | 220 | LED monitor | II | Stationary | Fail |  |  |  |  | Fail | 2022-03-10 | AMc | 1671 | Needs a UK plug fitting
| 221 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
| 222 | USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
Room29 | 223 | 6-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
Room29 | 224 | 4-way extension with USB | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
| 225 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-10 | AMc
| 226 | 5V 10A adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-10 | AMc
| 227 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-24 | AMc
| 228 | Philips 223V monitor | I | Portable | Pass | 0.01 | >20 | 0.31 | N/A | Pass | 2022-03-24 | AMc
| 229 | FSP laptop charger | II | Portable | Pass | N/A | >20 | 0.07 | N/A | Pass | 2022-03-24 | AMc
| 230 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-24 | AMc
| 231 | Technomate 4x12V power supply | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 232 | Benross heater | I | Portable | Pass | 0.01 | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 233 | 12V 2A power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 234 | 12V 1500mA power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 235 | 12V 1.5A power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 236 | Little Printer power supply | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 237 | USB adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 238 | MicroUSB adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 239 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-24 | AMc
| 240 | Lenovo power supply | II | Portable | Pass | N/A | >20 | 0.06 | N/A | Pass | 2022-03-24 | AMc
| 241 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-24 | AMc
| 242 | Sony Vaio power supply | II | Portable | Pass | N/A | >20 | 0.07 | N/A | Pass | 2022-03-24 | AMc
| 243 | Aiwa CA-W51 boombox | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-03-24 | AMc
| 244 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-24 | AMc
| 245 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-24 | AMc
| 246 | Short 4-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-24 | AMc
| 247 | Oil-filled radiator | I | Portable | Pass | 0.09 | 7.44 | 0.09 | N/A | Pass | 2022-03-24 | AMc
| 248 | Samsung "Made Invaders" monitor | I | Portable | Pass | 0.01 | >20 | 0.3 | N/A | Pass | 2022-03-31 | AMc
| 249 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-31 | AMc
Main Room | 250 | HP LaserJet M402dn printer | I | Stationary | Pass | 0.01 | >20 | 0.72 | N/A | Pass | 2022-03-31 | AMc
| 251 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-31 | AMc
Main Room | 252 | HP DesignJet 510 Queen Victoria printer | I | Stationary | Pass | 0.01 | >20 | 0.81 | N/A | Pass | 2022-03-31 | AMc
| 253 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-03-31 | AMc
Main Room | 254 | HP LaserJet Pro 200 colour printer | I | Stationary | Pass | 0.01 | >20 | 0.79 | N/A | Pass | 2022-03-31 | AMc
| 255 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-04-07 | AMc
| 256 | MCQN Lenovo X1 laptop | II | Portable | Pass | N/A | >20 | 0.05 | N/A | Pass | 2022-04-07 | AMc
| 257 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-04-07 | AMc
| 258 | PC power supply | I | Portable | Pass | 0.01 | >20 | 0.53 | N/A | Pass | 2022-04-07 | AMc
| 259 | PC power supply | I | Portable | Pass | 0.01 | >20 | 0.59 | N/A | Pass | 2022-04-07 | AMc
| 260 | PC power supply | I | Portable | Pass | 0.01 | >20 | 0.77 | N/A | Pass | 2022-04-07 | AMc
portable | 261 | Grey lamp | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
Main Room | 262 | 6-way long extension under East desks | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 263 | 8-way extension | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 264 | 6-way long extension under East desks | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
| 265 | 6-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
| 266 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
| 267 | Raspberry Pi adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
| 268 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 269 | 4-way long extension under East desks | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 270 | 4-way long extension under Eask desks | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
| 271 | 4-way switched extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
| 272 | 2-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
| 273 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 274 | Ultimaker power supply | I | Stationary | Pass | 0.01 | >20 | 1.35 | N/A | Pass | 2022-05-21 | AMc
Main Room | 275 | Priints Adam sonoff | Sonoff | Stationary | Pass | 0.01 | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
| 276 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 277 | Felicity's power supply | I | Stationary | Pass | 0.02 | >20 | 1.42 | N/A | Pass | 2022-05-21 | AMc
| 278 | Cocraft HMD150 rotary tool | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
| 279 | 12V charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
Main Room | 280 | 4-way for 3D printers | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
| 281 | 4-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 282 | 4-way for 3D resin 3D printers | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 283 | 4-way for 3D resin 3D printers | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 284 | Sonoff for Creality 3D printer | Sonoff | Stationary | Pass | 0.06 | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
| 285 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 286 | Creality 3D printer | I | Stationary | Pass | 0.09 | >20 | 0.41 | N/A | Pass | 2022-05-21 | AMc
Main Room | 287 | Raspberry Pi adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
Main Room | 288 | Red resin 3D printer | I | Stationary | Pass | 0.01 | >20 | 0.68 | N/A | Pass | 2022-05-21 | AMc
Main Room | 289 | Resin printer wash tank | I | Stationary | Pass | 0.01 | >20 | 0.16 | N/A | Pass | 2022-05-21 | AMc
| 290 | USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
| 291 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-21 | AMc
Main Room | 292 | Creality resin 3D printer | I | Stationary | Pass | 0.01 | >20 | 0.44 | N/A | Pass | 2022-05-21 | AMc
Main Room | 293 | Sonoff for Ender 3D printer | Sonoff | Stationary | Pass | 0.01 | >20 | 0.03 | N/A | Pass | 2022-05-21 | AMc
Main Room | 294 | Ender 3D printer | I | Stationary | Pass | 0.01 | >20 | 0.37 | N/A | Pass | 2022-05-21 | AMc
| 295 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-05-26 | PKH
Main Room | 296 | Roland EGX-300 CNC mill | I | Stationary | Pass | 0.01 | >20 | 0.34 | N/A | Pass | 2022-05-26 | PKH
| 297 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-11 | AMc
| 298 | PC power supply | I | Portable | Pass | 0.01 | >20 | 0.67 | N/A | Pass | 2022-06-11 | AMc
Matt's Desk | 299 | Orange extension lead | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Matt's Desk | 300 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Matt's Desk | 301 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Matt's Desk | 302 | Dell monitor | I | Stationary | Pass | 0.01 | >20 | 0.48 | N/A | Pass | 2022-06-16 | AMc
Matt's Desk | 303 | Lenovo power supply | II | Portable | Pass | N/A | >20 | 0.08 | N/A | Pass | 2022-06-16 | AMc
Matt's Desk | 304 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Matt's Desk | 305 | Dell monitor | I | Stationary | Pass | 0.01 | >20 | 0.51 | N/A | Pass | 2022-06-16 | AMc
Matt's Desk | 306 | One Beat 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Matt's Desk | 307 | TP-Link power adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-06-16 | AMc
Matt's Desk | 308 | 8-way extension | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Matt's Desk | 309 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Matt's Desk | 310 | Thermaltake server | I | Stationary | Pass | 0.01 | >20 | 0.62 | N/A | Pass | 2022-06-16 | AMc
Matt's Desk | 311 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Matt's Desk | 312 | Bitcoin server | I | Stationary | Pass | 0.01 | >20 | 0.75 | N/A | Pass | 2022-06-16 | AMc
| 313 | 4-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Room29 | 314 | Lightbox Gerda Taro | I | Stationary | Pass | 0.01 | >20 | 0.08 | N/A | Pass | 2022-06-16 | AMc
| 315 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
Room29 | 316 | Nalini's Mac | II | Stationary | Pass | N/A | >20 | 0.07 | N/A | Pass | 2022-06-16 | AMc
Room29 | 317 | Nalini's 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-06-16 | AMc
| 318 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-07-14 | AMc
Kitchen | 319 | Kitchen Geometric Lights power supply | I | Stationary | Pass | 0.06 | >20 | 1.09 | N/A | Pass | 2022-07-14 | AMc
Kitchen | 320 | Dishwasher | I | Stationary | Pass | 0.06 | >20 | 3.08 | N/A | Pass | 2022-07-14 | AMc
Kitchen | 321 | Bosch kettle | I | Stationary | Pass | 0.01 | >20 | 0.03 | N/A | Pass | 2022-07-14 | AMc |  | Earth point on the outside of the circular connector on the base
Kitchen | 322 | Daewoo Fridge | I | Stationary | Pass | 0.01 | >20 | 0.1 | N/A | Pass | 2022-07-14 | AMc
Kitchen | 323 | Bin power adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-07-14 | AMc
Kitchen | 324 | Tefal Toast N' Egg | I | Stationary | Pass | 0.03 | >20 | 0.03 | N/A | Pass | 2022-07-14 | AMc
Kitchen | 325 | Sonoff 4-way | Sonoff | Stationary | Fail |  |  |  |  | Fail | 2022-07-14 | AMc
| 326 | Equatech 4-way | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-07-21 | AMc
| 327 | Equatech 4-way | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-07-21 | AMc
| 328 | Equatech 4-way | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-07-21 | AMc
| 329 | Equatech 4-way | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-07-21 | AMc
| 330 | Equatech 4-way | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-07-21 | AMc
| 331 | Vacuum former | I | Stationary | Pass | 0.01 | 0.33 |  |  | Fail | 2022-08-18 | AMc | 1722
| 332 | Dell Studio XPS computer | I | Stationary | Pass | 0.01 | >20 | 0.5 | N/A | Pass | 2022-08-18 | AMc
| 333 | Leila Boxford CNC lathe | I | Stationary | Pass | 0.01 | >20 | 0.35 | N/A | Pass | 2022-08-18 | AMc
| 334 | Pink anglepoise lamp | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-08 | AMc
| 335 | IEC lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
| 336 | Epson Stylus Pro 9800 | I | Stationary | Pass | 0.08 | >20 | 0.38 | N/A | Pass | 2022-09-17 | AMc
| 337 | 4-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 338 | Cookwork espresso machine | I | Stationary | Pass | 0.07 | >20 | 0.04 | N/A | Pass | 2022-09-17 | AMc
| 339 | 4-way extension | Ext | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 340 | Desk 2-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 341 | Doorbell sounder | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
Main Room | 342 | Desk 2-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 343 | Desk 2-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 344 | Desk 2-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 345 | 6-way under West desks | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 346 | Desk 2-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 347 | 4-way under West desks | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Main Room | 348 | 2-way for coffee and 3D printers | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
Chris' Desk | 349 | USB adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
Chris' Desk | 350 | 12V 1A adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
Room29 | 351 | USB adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
Room29 | 352 | Phone power adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
Room29 | 353 | 4-way extension | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-17 | AMc
John's Desk | 354 | Variable DC adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
John's Desk | 355 | Variable DC adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
John's Desk | 356 | USB adapter | II | Portable | Pass | N/A | >20 | 0.06 | N/A | Pass | 2022-09-17 | AMc
John's Desk | 357 | DC adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
John's Desk | 358 | Phone DC adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-09-17 | AMc
John's Desk | 359 | Apple monitor | I | Stationary | Pass | 0.06 | >20 | 0.41 | N/A | Pass | 2022-09-17 | AMc
Events Room | 360 | Doorbot1 | I | Stationary | Pass | 0.02 | >20 | 0.25 | N/A | Pass | 2022-09-22 | AMc
Events Room | 361 | Geometric Lights | I | Stationary | Pass | 0.02 | >20 | 0.97 | N/A | Pass | 2022-09-22 | AMc |  | Ground tested against the power supply inside the wooden box
| 362 | Reel 2-way extension | Ext | Portable | Pass | 0.2 | >20 | N/A | Good | Pass | 2022-09-22 | AMc |  | 1.25mm^2 cable, Appendiix 5 of 5th Editiion code of practice gives 312mOhms for max RPE over the 20m of cable
Main Room | 363 | Doorbot2 | I | Stationary | Pass | 0.1 | >20 | 0.21 | N/A | Pass | 2022-09-22 | AMc
Main Room | 364 | IEC Lead | IEC | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-22 | AMc
Main Room | 365 | Doorbot2 Dell Monitor | I | Stationary | Pass | 0.05 | >20 | 0.56 | N/A | Pass | 2022-09-22 | AMc
| 366 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-22 | AMc
| 367 | Isolation transformer | I | Portable | Pass | 0.02 | >20 | 0.03 | N/A | Pass | 2022-09-22 | AMc |  | Ground tested against the sockets on the front
| 368 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-09-22 | AMc
Dinky | 369 | Ronan's 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 370 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 371 | Ronan's server 2 | I | Stationary | Pass | 0.06 | >20 | 0.73 | N/A | Pass | 2022-10-07 | AMc
| 372 | Ronan's server 4 | I | Stationary | Pass | 0.01 | >20 | 0.71 | N/A | Pass | 2022-10-07 | AMc
| 373 | Ronan's server 3 | I | Stationary | Pass | 0.01 | >20 | 0.7 | N/A | Pass | 2022-10-07 | AMc
| 374 | Ronan's server 1 | I | Stationary | Pass | 0.02 | >20 | 0.71 | N/A | Pass | 2022-10-07 | AMc
| 375 | Ronan's server 5 | I | Stationary | Pass | 0.06 | >20 | 0.72 | N/A | Pass | 2022-10-07 | AMc
| 376 | Ronan's server 6 | I | Stationary | Pass | 0.01 | >20 | 0.72 | N/A | Pass | 2022-10-07 | AMc
| 377 | Ronan's server 7 | I | Stationary | Pass | 0.01 | >20 | 0.72 | N/A | Pass | 2022-10-07 | AMc
| 378 | Ronan's 12-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 379 | Ronan's server 8 | I | Stationary | Pass | 0.01 | >20 | 0.7 | N/A | Pass | 2022-10-07 | AMc
| 380 | Ronan's server 10 | I | Stationary | Pass | 0.02 | >20 | 0.66 | N/A | Pass | 2022-10-07 | AMc
| 381 | Ronan's server 12 | I | Stationary | Pass | 0.03 | >20 | 0.66 | N/A | Pass | 2022-10-07 | AMc
| 382 | Ronan's server 14 | I | Stationary | Pass | 0.09 | >20 | 0.67 | N/A | Pass | 2022-10-07 | AMc
| 383 | Ronan's server 16 | I | Stationary | Pass | 0.06 | >20 | 0.64 | N/A | Pass | 2022-10-07 | AMc
| 384 | Ronan's server 18 | I | Stationary | Pass | 0.04 | >20 | 0.65 | N/A | Pass | 2022-10-07 | AMc
| 385 | Ronan's server 20 | I | Stationary | Pass | 0.03 | >20 | 0.67 | N/A | Pass | 2022-10-07 | AMc
| 386 | Ronan's server 22 | I | Stationary | Pass | 0.02 | >20 | 0.66 | N/A | Pass | 2022-10-07 | AMc
| 387 | Ronan's server 24 | I | Stationary | Pass | 0.02 | >20 | 0.66 | N/A | Pass | 2022-10-07 | AMc
| 388 | Ronan's Netgear router "Internet" | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-10-07 | AMc
| 389 | Ronan's 4-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 390 | Ronan's Netgear router "Internal" | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-10-07 | AMc
| 391 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 392 | Ronan's Netgear adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-10-07 | AMc
| 393 | Ronan's Netgear adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-10-07 | AMc
| 394 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 395 | Ronan's black 4-way | Ext | Stationary | Pass | 0.03 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 396 | Ronan's USB adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-10-07 | AMc
| 397 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 398 | Ronan's Dell PC | I | Stationary | Pass | 0.09 | >20 | 0.38 | N/A | Pass | 2022-10-07 | AMc
| 399 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 400 | Ronan's Black PC | I | Stationary | Pass | 0.07 | >20 | 0.89 | N/A | Pass | 2022-10-07 | AMc
| 401 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 402 | Ronan's UPS | I | Stationary | Pass | 0.01 | >20 | 0.18 | N/A | Pass | 2022-10-07 | AMc
| 403 | Long 2-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 404 | Ronan's switched 12-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-07 | AMc
| 405 | Ronan's server 9 | I | Stationary | Pass | 0.06 | >20 | 0.69 | N/A | Pass | 2022-10-07 | AMc
| 406 | Ronan's server 11 | I | Stationary | Pass | 0.02 | >20 | 0.68 | N/A | Pass | 2022-10-07 | AMc
| 407 | Ronan's server 13 | I | Stationary | Pass | 0.01 | >20 | 0.67 | N/A | Pass | 2022-10-07 | AMc
| 408 | Ronan's server 15 | I | Stationary | Pass | 0.02 | >20 | 0.64 | N/A | Pass | 2022-10-07 | AMc
| 409 | Ronan's server 17 | I | Stationary | Pass | 0.01 | >20 | 0.66 | N/A | Pass | 2022-10-07 | AMc
| 410 | Ronan's server 19 | I | Stationary | Pass | 0.03 | >20 | 0.67 | N/A | Pass | 2022-10-07 | AMc
| 411 | Ronan's server 21 | I | Stationary | Pass | 0.02 | >20 | 0.69 | N/A | Pass | 2022-10-07 | AMc
| 412 | Ronan's server 23 | I | Stationary | Pass | 0.01 | >20 | 0.66 | N/A | Pass | 2022-10-07 | AMc
| 413 | Ronan's Samsung monitor | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-10-07 | AMc
| 414 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-10-16 | MAG
| 415 | PBS800C belt sander | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-10-16 | MAG
CNC Room | 416 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-11-24 | AMc
CNC Room | 417 | CNC router computer | I | Stationary | Pass | 0.06 | >20 | 0.92 | N/A | Pass | 2022-11-24 | AMc
CNC Room | 418 | CNC router 6-way | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-11-24 | AMc
CNC Room | 419 | WorkZone router table | I | Portable | Pass | 0.01 | >20 | 0.03 | N/A | Pass | 2022-11-24 | AMc
CNC Room | 420 | Clarke air compressor | I | Stationary | Pass | 0.01 | >20 | 0.09 | N/A | Pass | 2022-11-24 | AMc
CNC Room | 421 | CNC router | I | Stationary | Pass | 0.01 | >20 | 0.93 | N/A | Pass | 2022-11-24 | AMc
CNC Room | 422 | CNC router sonoff | Sonoff | Stationary | Pass | 0.01 | >20 | 0.03 | N/A | Pass | 2022-11-24 | AMc
CNC Room | 423 | 4-way on top of CNC router cabinet | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-08 | AMc
CNC Room | 424 | Light for CNC cabinet | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-01-19 | AMc | 1744
CNC Room | 425 | Makita handheld router | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-08 | AMc
CNC Room | 426 | Ryobi circular saw | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-08 | AMc
CNC Room | 427 | Hilka 6" Bench Grinder | I | Stationary | Pass | 0.02 | >20 | 0.06 | N/A | Pass | 2022-12-08 | AMc
Network Closet | 428 | 5-way switched extension | Ext | Stationary | Pass | 0.05 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Network Closet | 429 | CCTV Pi power supply | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Network Closet | 430 | Netgear 8-port switch | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Network Closet | 431 | Amazon Pi power supply | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Network Closet | 432 | Mickey-mouse lead | IEC | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Network Closet | 433 | Unifi WAN box | II | Stationary | Pass | N/A | >20 | 0.2 | N/A | Pass | 2022-12-30 | AMc
Network Closet | 434 | Variable DC adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Network Closet | 435 | Mickey-mouse lead | IEC | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Network Closet | 436 | Baltic Broadband router | II | Stationary | Pass | N/A | >20 | 0.19 | N/A | Pass | 2022-12-30 | AMc
Network Closet | 437 | 8-way extension | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Network Closet | 438 | IEC Lead | IEC | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Network Closet | 437 | Unifi Switch 16 | I | Stationary | Pass | 0.06 | >20 | 0.84 | N/A | Pass | 2022-12-30 | AMc
Network Closet | 438 | IEC Lead | IEC | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Network Closet | 439 | Dell Powerconnect 5548 | I | Stationary | Pass | 0.01 | >20 | 0.65 | N/A | Pass | 2022-12-30 | AMc
| 440 | Netgear Prosafe 24-port switch | I | Stationary | Pass | 0.05 | >20 | 1 | N/A | Pass | 2022-12-30 | AMc
| 441 | Micro-USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Christmas Decorations | 442 | 24VAC adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Christmas Decorations | 443 | Green net lights | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Christmas Decorations | 444 | Multi-coloured string of fairy lights | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Jackie's Desk | 445 | IEC Lead | IEC | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Jackie's Desk | 446 | 4A USB charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Jackie's Desk | 447 | 5V 2A power supply | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Jackie's Desk | 448 | Mickey-mouse lead | IEC | Portable | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Jackie's Desk | 449 | Dell laptop power supply | II | Portable | Pass | N/A | >20 | 0.06 | N/A | Pass | 2022-12-30 | AMc
Jackie's Desk | 450 | Philips monitor | I | Portable | Pass | 0.04 | >20 | 0.31 | N/A | Pass | 2022-12-30 | AMc
Jackie's Desk | 451 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Jackie's Desk | 452 | Dell laptop power supply | II | Portable | Pass | N/A | >20 | 0.07 | N/A | Pass | 2022-12-30 | AMc
Jackie's Desk | 453 | Switched USB-C charger | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Jackie's Desk | 454 | TP-Link power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2022-12-30 | AMc
Jackie's Desk | 455 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2022-12-30 | AMc
Jackie's Desk | 456 | LED Flowers | I | Portable | Pass | 0.07 | >20 | 0.17 | N/A | Pass | 2022-12-30 | AMc
Ben's Desk | 457 | HP monitor | I | Stationary | Pass | 0.01 | >20 | 0.87 | N/A | Pass | 2022-12-30 | AMc
Main Room | 458 | JJ XY Plotter | I | Stationary | Pass | 0.03 | >20 | 0.05 | N/A | Pass | 2023-03-11 | MAG
MAIN ROOM | 459 | Injection Moulder | II | Stationary | Pass | 0.06 | >20 | 0.13 | N/A | Pass | 2023-03-11 | MAG
Main Room | 460 | PC Power Supply | I | Stationary | Pass | 0.02 | >20 | 0.34 | N/A | Pass | 2022-12-30
Laser Room | 461 | Dyson vacuum cleaner | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-03-25 | AMc
Laser Room | 462 | Startrite bandsaw | I | Stationary | Pass | 0.07 | >20 | 0.04 | N/A | Pass | 2023-03-25 | AMc
Laser Room | 463 | 2-way for extraction | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-03-25 | AMc
Laser Room | 464 | Main extraction fan | I | Stationary | Pass | 0.03 | >20 | 0.06 | N/A | Pass | 2023-03-25 | AMc | 1784
Laser Room | 465 | Chiller for Tony | I | Stationary | Pass | 0.02 | >20 | 0.05 | N/A | Pass | 2023-03-25 | AMc
Laser Room | 466 | TP-Link power adapter | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-03-25 | AMc
Laser Room | 467 | Mickey-mouse lead | IEC | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-03-25 | AMc
Laser Room | 468 | Lenovo power supply | II | Stationary | Pass | N/A | >20 | 0.06 | N/A | Pass | 2023-03-25 | AMc
Laser Room | 469 | IEC Lead | IEC | Lead | Pass | 0.03 | >20 | N/A | Good | Pass | 2023-03-25 | AMc
Laser Room | 470 | AOC monitor for Tony | I | Stationary | Pass | 0.1 | >20 | 0.37 | N/A | Pass | 2023-03-25 | AMc
Laser Room | 471 | 4-way for Tony | Ext | Stationary | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-03-25 | AMc
Laser Room | 472 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-03-25 | AMc
Laser Room | 473 | Chiller for Gerald | I | Stationary | Pass | 0.06 | >20 | 0.18 | N/A | Pass | 2023-03-25 | AMc
Laser Room | 474 | Switched extension for Gerald | Ext | Stationary | Pass | 0.05 | >20 | N/A | Good | Pass | 2023-03-25 | AMc |  | Also tested with the switch in the off position to confirm it fails with polarity "open"
Laser Room | 475 | Sonoff for Gerald | Sonoff | Stationary | Pass | 0.01 | >20 | 0.03 | Open | Pass | 2023-03-25 | AMc
Laser Room | 476 | Gerald Laser-cutter | I | Stationary | Pass | 0.04 | 1.03 | 2.62 | N/A | Pass | 2023-03-25 | AMc | 1787
| 477 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-03-30 | AMc
| 478 | IEC extension | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-03-30 | AMc
| 479 | IEC 3-way extension | Ext | Portable | Pass | 0.09 | >20 | N/A | Good | Pass | 2023-03-30 | AMc
| 480 | HP square monitor | I | Portable | Pass | 0.06 | >20 | 0.8 | N/A | Pass | 2023-03-30 | AMc
| 481 | Dell monitor | I | Portable | Pass | 0.01 | >20 | 0.59 | N/A | Pass | 2023-03-30 | AMc
| 482 | Dell monitor | I | Portable | Pass | 0.01 | >20 | 0.54 | N/A | Pass | 2023-03-30 | AMc
| 483 | Dell monitor | I | Portable | Pass | 0.02 | >20 | 0.59 | N/A | Pass | 2023-03-30 | AMc
| 484 | Samsung monitor | I | Portable | Pass | 0.01 | >20 | 0.17 | N/A | Pass | 2023-03-30 | AMc
| 485 | Bush small fridge | I | Stationary | Pass | 0.07 | >20 | 0.09 | N/A | Pass | 2023-03-30 | AMc
| 486 | Claire vacuum former | I | Stationary | Pass | 0.01 | >20 | 0.62 | N/A | Pass | 2023-04-20 | AMc | 1788 | Also tested with the protective conductor current test, which didn't get above 0.44mA
| 487 | Vacuum pump | I | Portable | Pass | 0.01 | >20 | 0.1 | N/A | Pass | 2023-03-30 | AMc
Jackie's desk | 488 | LG monitor | II | Stationary | Pass | N/A | >20 | 0.14 | N/A | Pass | 2023-03-30 | AMc
| 489 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-03-30 | AMc
Main Room | 490 | Creality 3D printer | I | Stationary | Pass | 0.05 | >20 | 0.62 | N/A | Pass | 2023-03-30 | AMc
| 491 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | AMc
Laser Room | 492 | Sheila's PC | I | Stationary | Pass | 0.09 | >20 | 0.41 | N/A | Pass | 2023-04-08 | AMc
| 493 | Hnady Power polisher | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-04-08 | AMc
Laser Room | 494 | Laser-cutter Tony | I | Stationary | Pass | 0.8 | 1 | 4.95 | N/A | Pass | 2023-04-08 | AMc
Adrian's desk | 495 | Starbook laptop power supply | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-04-08 | AMc
| 496 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | AMc
Electronics area | 497 | CircuitSpecialists CSI3005X5 Bench Power Supply | I | Portable | Pass | 0.05 | >20 | 0.05 | N/A | Pass | 2023-04-08 | RC
| 498 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | RC
| 499 | 4-way extension | Ext | Ext | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | RC
| 500 | 4-way extension | Ext | Ext | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | RC
| 501 | Bionaire desk fan | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-04-08 | RC
| 502 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | RC
| 503 | Masscot 12VDC adapter | II | Portable | Pass | N/A | >20 | 0.03 | Good | Pass | 2023-04-08 | RC
| 504 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | RC
| 505 | Blue Powergeek USB charger | II | Portable | Pass | N/A | >20 | 0.17 | N/A | Pass | 2023-04-08 | RC
| 506 | Teal Powergeek USB charger | II | Portable | Pass | N/A | >20 | 0.17 | N/A | Pass | 2023-04-08 | RC
| 507 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | RC
| 508 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-08 | RC
| 509 | Xerox Phaser 7100 colour laser-printer | I | Stationary | Pass | 0.03 | >20 | 0.32 | N/A | Pass | 2023-04-08 | RC
| 510 | 2-way extension | Ext | Ext | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-13 | AMc
| 511 | Protective Conductor Current Tester | Ext | Portable | Pass | 0.04 | >20 | N/A | Good | Pass | 2023-04-27 | AMc
Room29 | 512 | Automated Blinds | II | Stationary | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-04-27 | AMc
Alex's Desk | 513 | 12V 1.5A power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-04-27 | AMc
Alex's Desk | 514 | Polaroid Monitor | II | Portable | Pass | N/A | >20 | 0.23 | N/A | Pass | 2023-04-27 | AMc
Alex's Desk | 515 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-27 | AMc
Alex's Desk | 516 | 12V 1A power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-04-27 | AMc
Alex's Desk | 517 | 12V 1A power adapter | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-04-27 | AMc
Alex's Desk | 518 | Mickey-mouse lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-04-27 | AMc
Alex's Desk | 519 | Lenovo power supply | II | Portable | Pass | N/A | >20 | 0.08 | N/A | Pass | 2023-04-27 | AMc
Alex's Desk | 520 | Iiyama monitor | I | Stationary | Pass | 0.02 | >20 | 0.42 | N/A | Pass | 2023-04-27 | AMc
Alex's Desk | 521 | Uni-T bench multimeter | II | Portable | Pass | N/A | >20 | 0.05 | N/A | Pass | 2023-04-27 | AMc
| 522 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-07-16 | MAG
| 523 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-07-16 | MAG
Workshop | 524 | Mini plotter Power Supply | II | Portable | Pass | N/A | >20 | 0.03 | Good | Pass | 2023-08-20 | MAG
| 525 | IEC Lead | IEC | Lead | Pass | 0.01 | >20 | N/A | Good | Pass | 2023-08-20 | MAG
Workshop | 526 | Wax Melting Pot | I | Portable | Pass | 0.01 | >20 | 0.03 | Good | Pass | 2023-08-20 | MAG
Workshop | 527 | 24V Power Supply | II | Portable | Pass | N/A | >20 | 0.03 | Good | Pass | 2023-08-20 | MAG
| 528 | 6V power supply | II | Portable | Pass | N/A | >20 | 0.03 | N/A | Pass | 2023-09-09 | AMc